# HYGRODYNAMICS

DEW POINT TRANSMITTER BOARD

#### 6380NR – 115V

6380NR – 24V

# TABLE OF CONTENTS

GENERAL DESCRIPTION							2

SPECIFICATIONS								2

INSTALLATION								2

OPERATION									3

Board Power 								3

Ground									4

Signal Outputs								4

Sensor Input								4

MAINTENANCE								4

CIRCUIT TEST PROCEDURE					    	4

LIMITED WARRANTY							5

DIAGRAMS

TRANSMITTER WIRING- 6380WD

NEWPORT SCIENTIFIC, INC.

8246-E SANDY COURT

JESSUP, MD  20794-9632

(301) 498-6700   FAX: (301) 490-2313   E-MAIL NEWPORT888@AOL.COM

ADMIN/MANUAL/6380NR									FEBRUARY 2002

##### GENERAL DESCRIPTION

The 6380NR Transmitter is designed to provide a linear dew point representation with a 0-5VDC or 4-20mA output signal.  The transmitter uses digital and high precision analog circuitry which requires no field calibration.

Dew point measurement is accomplished with the low cost Hygrosensor® Part Number 1205DM.  This sensor is interchangeable and can be easily replaced in the field.

SPECIFICATIONS

Operating Voltage				6380NR-115VAC	95VAC - 130VAC

###### 6380NR-24V		18VDC - 26VDC

Operating Temperature			32F to 122F

Range of Electronics

Dew point Range				-40F to +15F

Maximum Sensor Temperature		140F

Typical Accuracy				+2F

Output Signal Load

4-20mA				500 MAX			                                 	0-5VDC	    	               	1k MIN

PC Board Dimensions			2.81" W X 3.66" L

Ma  = (DP +53.8)/3.44

V  =  (DP +40)/11

INSTALLATION

For 0-300psig-pipe installation, use the following:

6146A   - 1" NPT Sensor Mount

6020-72 - 6 foot Cable (other sizes available)

1205DM  - Sensor

For 0-100psig remote installation, use the following:

3300101 - Manifold

1000613 - Gasket

0900106 - 2 Pin Plastic Insert

4600202 - Hex Nut

6020-72 - 6 foot Cable (other sizes available)

1205DM  - Sensor

Choose a suitable location for the transmitter board and perform these steps:

1)	For line powered models set jumpers J1, J2, and J3 for operating voltage.

Supply:	115VAC		230VAC

Install:		J1 and J3		J2

2)	Mount transmitter PC board to panel.  Refer to Wiring Diagram for mounting dimensions.

3)	Wire the terminal block as shown below. The terminal block can be unplugged for easy wiring.

Terminal H	AC Line Hot (+ for DC operation)

Terminal N	AC Line Neutral (- for DC operation)

Terminal G	Power Ground

Terminal V	0-5VDC Output (0V = -40F 5V = +15F)

Terminal M	4-20mA Output (4mA = -40F 20mA = +15F)

Terminal S	Sensor Input (a)

Terminal S	Sensor Input (b)

Terminal G	Signal Ground

OPERATION

Board Power

Line powered boards will function with supply voltages in the range listed in the Specification Table.  The on-board power supply includes over-voltage protection and surge suppression and can be used with confidence in noisy electrical environments.

24V models have on-board regulation and protection.  Circuit performance is guaranteed within the voltage range listed in the specification table.  Board operation is immune to 60Hz or 120Hz ripple as long as peak voltages remain in the operating range.

Ground

Power ground and Signal ground are connected together on the board.  The lower left mounting hole is connected to this ground as well.  If the board is mounted to a grounded chassis, this is normally the only ground connection required.  The signal outputs are referenced to this ground.

Some sensor cables may have a ground wire.  In this case, the sensor ground can conveniently be wired to terminal 8.

Signal Outputs

The system provides linear 4-20mA and 0-5VDC output signals representing -40F to +15F dew point.  Both outputs can be used simultaneously without any interaction between the two.

Both outputs are short circuit protected.

Sensor Input

The sensor cable connects to sensor (a) and sensor (b) terminals.  The sensor is not polarized so wiring polarity is irrelevant.  If the sensor cable has a ground shield (used on some long cable applications) connect the shield to terminal 3 or 8.

After initial exposure of the sensor to dry air, system will respond quickly to changes in dew point.  Ideally, sample airflow should be 5 SCFH or greater.  Less flow will not affect accuracy but will result in slower response.

##### MAINTENANCE

No calibration of the circuit is necessary.  However, sensor should be replaced annually to maintain system response and accuracy.  If the electronics are thought to be defective, perform the Circuit Test described below.

CIRCUIT TEST

With power still applied, disconnect sensor cable at transmitter. Output should settle to 4.0mA,(+0mA)(-0.2mA) or (0.00VDC +0.05).  Process indicator should read -40F.

Connect a jumper across the sensor input terminals (a) and (b).  Output should reach 20.0mA, + 0.2mA (5.0VDC + 0.05VDC).  Process indicator should read 15F.If transmitter does not function properly, contact factory.

## HYGRODYNAMICS

# LIMITED WARRANTY

NEWPORT  SCIENTIFIC,  INC.  warrants that all  equipment manufactured  by  NSI  shall  be  free  from defects in  material  and  workmanship which  might  impair its  usefulness.  SELLER DOES  NOT WARRANT  THAT THE EQUIPMENT IS FIT FOR ANY PARTICULAR USE.  THERE ARE NO WARRANTIES WHICH  EXTEND  BEYOND  THE  DESCRIPTION  ON   THE  FACE  HEREOF;  the obligation under this warranty is limited to  repairing or replacing, at Seller's factory, any defective parts which,  when returned by the buyer,  TRANSPORTATION PREPAID,  examination  discloses to  have been factory  defective.  The  time limit of  this  warranty is  ONE  YEAR from  date of  shipment of new  equipment,  SIX MONTHS  from  date of shipment  of Hygrodynamics  Wide-Range Sensors  and THREE MONTHS from date  of shipment of  Hygrodynamics Narrow-Range Sensors and repaired equipment.  THIS WARRANTY IS  EXPRESSLY IN LIEU OF  OTHERWARRANTIES.Seller  shall  not  be  held  liable   for  any  special,   indirect, consequential  damages arising  out of  this warranty  or any  breach thereof,  of any defect in or failure or malfunction of the equipment and  materials  are  further  subject  to  tolerances  and variations  consistent  with  usages of trade.  This warranty  shall run in favor only  of  the purchaser  from Seller  and  may  not be  passed  on or represented on behalf of Seller to any subsequent purchaser.

### WARRANTIES: OTHER PRODUCTS

NEWPORT SCIENTIFIC, INC.  makes no express or  implied warranty as to items,  which are the  products of other manufacturers.  Seller shall use its best efforts to  obtain from the  manufacturer, in accordance with  its  customary  practice,  the  repair  or  replacement of such products   may  prove  defective  in  workmanship  or  material.  The foregoing  states the entire  liability in respect  to such products,except  as an authorized  executive of the  corporation may otherwise agree in writing.

In  the  case of  special  equipment  or  modifications  to  standard equipment   manufactured  at   the  request  of   the  buyer,   under buyer-approved  specifications,  buyer will indemnify  Seller against

the risk damages due to patent infringement.